# GridSenpAI Data Schema Documentation

# 1. Purpose

Define the structured data schemas used by GridSenpAI for ingesting facility engineering data and producing transmission-planning-ready model outputs. This document references where IBM Watson products are used for ingestion, parsing, and retrieval.

# 2. Input Data Schema (Facility Inputs)

Input data may be supplied via structured forms, API calls, or extracted from documents. Document ingestion (IBM Watson Discovery) and parsing (IBM Watson Discovery + watsonx.ai) populate the schema.

## 2.1 Core Inputs

facility_info: POI voltage (kV), service configuration, phased buildout schedule (MW by date/phase)

one_line_diagram: file reference(s) for MV/LV one-lines and substation diagrams

load_composition: IT MW, cooling MW, other MW; notes on power capping/demand management

ups_systems: vendor, model, topology, operating mode, rated kW, module count, redundancy

generators: vendor, model, rated kW, quantity, islanding/export capability, transfer mode

transformers: MVA rating, percent impedance, primary/secondary voltages, tap range if known

protection_settings: UV/UF/OV/OF curves; relay model and settings summary if available

harmonics: expected THDi/THD, filters present, major power-electronics sources

## 2.2 Units, Ranges, and Validation Rules

All power values must declare units (MW, Mvar, kVA/kW) and be normalized to MW/Mvar for outputs.

Voltage values must be normalized to kV.

Curves must be represented as time-value pairs (e.g., [(Vpu, seconds), ...]).

Unknown values must be null/omitted—not fabricated; missing critical items must trigger follow-up questions.

# 3. Output Data Schema (TP Outputs)

Outputs are produced by the Translation Engine (watsonx.ai + rules) and packaged for planners. Outputs must conform to the outputs schema and include provenance and confidence tags.

## 3.1 Output Categories

steady_state: Pmax/Pmin, Q limits, PF target or control mode

zip_model: aP/bP/cP and aQ/bQ/cQ (constant power/current/impedance fractions)

dynamic_parameters: voltage/frequency sensitivity, recovery constants, trip curves, reconnect logic

load_composition: electronic/motor/VFD/static fractions

ramping: max ramp up/down, step sizes, restoration pickup profiles (if known)

generator_interactions: islanding/export/closed transition flags and constraints

power_quality: harmonic risk screen and study recommendation

confidence_tags + provenance: evidence references and assumption list

# 4. Provenance and Confidence

Every output parameter must include provenance: source doc + passage ID (from Watson Discovery) or a rule reference.

Confidence levels: High (direct spec/settings), Medium (equipment-class inference), Low (assumption pending confirmation).

Scenario sets: Typical, Conservative, Best-case must be generated when key dynamics are uncertain.

# 5. Watson-Specific Data Integration Notes

Watson Discovery project collections should be segmented by customer/project to enforce isolation.

Discovery enrichments should extract entities like equipment names, ratings, and settings into structured fields.

watsonx.ai prompts should output strictly-valid JSON conforming to the schema with explicit nulls for unknowns.