# GridSenpAI Parameter Mapping Table (Facility Inputs → TP Outputs)

This table is the core translation reference used by GridSenpAI. It defines what facility-side inputs are needed, where supporting evidence is retrieved (RAG (IBM Watson Discovery + watsonx.ai)), how the translation is performed, and which TP-ready output parameters are produced. Confidence is expected to vary by evidence availability; missing inputs trigger follow-up questions.

# 1. Mapping Table

| Facility Input (What DC EE Provides) | RAG Evidence Sources (Watson) | Translation Logic (Rules / Inference) | TP Output Parameter(s) | Confidence Drivers / Notes |
| --- | --- | --- | --- | --- |
| POI voltage level(s), service configuration | Interconnection request docs; utility service standards; substation docs (Watson Discovery) | Normalize kV levels; validate consistent with one-line; assign POI bus representation | steady_state.Pmax/Pmin context; metadata for bus modeling | High if explicit in interconnection docs; Medium if inferred from one-line only |
| Phased buildout schedule (MW by date/phase) | Project schedule docs; load letter of intent; planning forms (Watson Discovery) | Generate per-phase Pmax/Pmin envelopes and scenario timelines | steady_state.Pmax/Pmin per phase; ramping profiles by phase | High if formal schedule exists; Low if only verbal estimates |
| One-line diagram (MV/LV) and equipment schedule | One-line PDFs/DWGs, equipment schedules (Watson Discovery) | Extract topology cues, transformer ratings, ATS placement; identify major load blocks | load_composition fractions; flags; transformer metadata | Medium: diagrams show topology but not dynamic behavior |
| IT load vs cooling load vs other load split | Load calcs; mechanical schedules; power budgets (Watson Discovery) | Compute composition fractions; infer motor/VFD share from cooling design | load_composition.electronic/motor/vfd/static; zip_model bounds | High when load studies provided; Medium when inferred |
| UPS vendor/model, topology (double conversion/eco), operating mode policy | UPS datasheets and manuals (Watson Discovery) | Map topology to constant-power behavior; set electronic fraction assumptions; note ride-through intent | zip_model (aP/bP/cP); dynamic_parameters.voltage_sensitivity; power_quality harmonic risk | High if explicit mode policy + spec; Medium otherwise |
| UPS rectifier type + THDi/THD specs; filters present | UPS power quality sections; harmonic standards references (Watson Discovery) | Assign harmonic risk score; decide if harmonic study recommended | power_quality.harmonic_risk; harmonic_study_recommended | High if THDi provided; Medium if inferred from rectifier type |
| Battery/energy storage autonomy and transfer behavior | UPS manuals; battery system submittals (Watson Discovery) | Infer ride-through capability window; define fault ride-through assumptions/bounds | dynamic_parameters.trip_voltage_curve (if known) or scenario bounds; recovery_time | Medium: autonomy known but grid behavior depends on controls |
| Generator count, model, kW rating, paralleling gear, export policy | Generator datasheets; controls manuals; interconnection agreements (Watson Discovery) | Set generator_interactions flags; define islanding behavior; constrain export to false if blocked | generator_interactions.islanding/export/closed_transition; dynamic scenario notes | High if interconnection agreement states export policy; Medium if only design intent |
| ATS type (open vs closed transition) and transfer sequence timing | ATS submittals; commissioning scripts (Watson Discovery) | Estimate load step/drop during transfer; define ramping/step behavior bounds | ramping.step_size_mw; dynamic_parameters.recovery_time; scenario cases | Medium; depends on commissioning settings |
| Transformers: MVA, %Z, vector group, taps | Transformer datasheets and test reports (Watson Discovery) | Validate ratings; provide short-circuit and voltage drop context; flag protection impacts | steady_state constraints; study notes (not always in output schema) | High if nameplate/test report present |
| Protection relay model + UV/UF/OV/OF settings at PCC | Relay settings exports; protection study report (Watson Discovery) | Translate curves into trip_* arrays; define ride-through assumptions if curves absent | dynamic_parameters.trip_voltage_curve; trip_frequency_curve | High if settings provided; Low if unknown |
| Cooling system design: chiller type, VFD usage, motor HP totals | Mechanical schedules; VFD datasheets (Watson Discovery) | Compute motor/vfd fractions; infer dynamic recovery characteristics | load_composition.motor/vfd fractions; zip_model coefficients bounds | Medium; depends on operating points |
| Ramping expectations: max MW/min, step energization plan | Commissioning plan; operations procedures (Watson Discovery) | Populate ramping limits; generate typical vs conservative scenarios | ramping.max_ramp_up/down; step_size_mw; scenario variants | High if commissioning plan exists; Medium otherwise |
| Power factor / reactive power control policy | Electrical basis-of-design; utility requirements (Watson Discovery) | Set PF target and Q limits; choose fixed PF vs voltage control intent | steady_state.power_factor_target; qmax/qmin if known | High if utility requirement documented |
| Power management software / demand response capabilities (if any) | Operations docs; EMS/BMS descriptions (Watson Discovery) | Define optional ramp limiting and curtailment flags; note for planners | ramping limits; notes in packet; may not map to core schema fields | Low to Medium; often proprietary or not documented |

# 2. Follow-Up Question Generation Rules

If trip curves are missing: ask for relay settings export or protection study summary at PCC.

If UPS operating mode policy is missing: ask whether double conversion is always enabled, and whether eco/bypass is permitted.

If export policy is ambiguous: ask whether generators are interlocked to prevent export and whether closed transition is enabled.

If cooling composition is unclear: ask for motor HP totals and whether major motors are VFD-controlled.

If ramping plan is missing: ask for commissioning energization step schedule and max ramp constraints.

# 3. Output Quality Requirements

Every mapping must either include evidence references or mark the resulting outputs as assumptions with Low confidence.

When uncertain, generate Typical/Conservative/Best-case scenarios rather than a single set of parameters.

All numeric outputs must include unit normalization and bounds checking.