# GridSenpAI Translation Engine Algorithm Specification

# 1. Purpose

Specify the translation logic that converts facility engineering artifacts into transmission planning model parameters. This document is written for implementation using RAG (IBM Watson Discovery + watsonx.ai) plus deterministic rule layers for unit normalization, bounds enforcement, and schema validation.

# 2. Inputs and Outputs

Inputs: structured facility schema populated from document parsing (IBM Watson Discovery + watsonx.ai) and direct user entries. Supporting evidence retrieved via RAG (IBM Watson Discovery + watsonx.ai). Outputs: TP parameter schema including steady-state, ZIP, dynamic parameters, composition, ramping, and confidence/provenance.

# 3. Pipeline Stages

## 3.1 Ingestion and Parsing

Ingest facility documents. Document ingestion (IBM Watson Discovery).

Parse one-lines/specs to extract equipment list, ratings, topology cues, and settings. Document parsing (IBM Watson Discovery enrichments + watsonx.ai).

Normalize units and names to canonical identifiers (e.g., kW→MW; kVA→MW using PF where known).

## 3.2 Retrieval (Grounding)

For each extracted equipment item (UPS, generator, VFD, relay), retrieve relevant datasheet sections and operational behavior notes. RAG (IBM Watson Discovery + watsonx.ai).

Retrieve modeling guidance documents applicable to the target region/ISO if provided; otherwise use default modeling references.

Return evidence passages with IDs for provenance.

## 3.3 Behavioral Feature Extraction

Identify UPS topology (double conversion vs eco/bypass), input rectifier type, and ride-through intent.

Identify generator operating policy (island-only vs parallel, export allowed/blocked, transfer mode).

Estimate load composition fractions: IT/electronic vs cooling motor/VFD vs static.

Extract protection trip/ride-through curves (UV/UF/OV/OF) when available; otherwise mark as missing and use scenario bounds.

## 3.4 Mapping Rules (Deterministic + Model-Assisted)

GridSenpAI uses a hybrid approach: deterministic rules for conversions and guardrails; model-assisted inference for classification and defaults when evidence exists.

Unit conversion and validation are deterministic (no AI).

Classification (e.g., UPS mode implies constant-power behavior) may be model-assisted but must cite evidence.

If no evidence is retrieved, output must include an assumption with Low confidence and a follow-up question.

## 3.5 Equivalent Load Model Generation

Compute P/Q envelopes at the POI for each buildout phase.

Generate ZIP coefficients based on composition + evidence; produce bounds when uncertain.

Generate dynamic parameters: voltage/frequency sensitivity, recovery time constants, and trip/reconnect logic where supported.

Generate scenario variants: Typical, Conservative, Best-case.

## 3.6 Provenance and Confidence

Attach evidence references (Watson Discovery document ID + passage/snippet reference) to each parameter.

Assign confidence levels per parameter and per scenario.

Create a missing-data list with the exact question to ask, tied to the parameter impacted.

# 4. Failure Modes and Handling

Unreadable one-line diagram → request clearer file or supplemental equipment schedule; proceed with partial data if possible.

Conflicting values across documents → flag conflict, present both, and request authoritative source.

Missing trip curves or controls policy → generate scenario bounds and follow-up questions; do not fabricate.

# 5. Outputs

Machine-readable JSON output conforming to GridSenpAI_outputs_schema.json.

Human-readable modeling packet summarizing assumptions, bounds, and evidence citations.

Changelog when regenerating outputs from updated inputs.